SD600 AC Drive PC Terminal Communication Software Operation Instructions

- Open Software

Find the location where the application is placed, click to enter the folder, find the executable program whose icon name is RWTools.exe, double-click to open the program, and enter the software interface as shown below:

Note: Before opening the program, you must store the configuration file: parameter.xls in the config folder, otherwise the software will not be able to open normally; these two files are edited and modified by the software provider, generally do not edit this file.

- Communication Parameter Configuration

Click the software interface icon，and the following communication configuration dialog box will appear. In order to establish normal communication with the AC Drive and realize effective data exchange, first set a reasonable communication data format.

Select the serial port number, baud rate, data format, and address number used for the current communication. The baud rate, data format, and address number must be the same as the drive parameter settings. For example, the above communication configuration corresponds to the SD600 series AC Drive parameter settings. As follows:

F18.00=1 address number      F18.01=45 baud rate         F18.02=3 Data format

After setting,click the icon to complete the connection, so as to realize the parameter reading and writing and data monitoring of the AC Drive.

- Read and Write Parameters

Click the icon,the software interface is as follows:

- 、Read current page parameters

Click the button, put the currently selected parameter group，for example all parameters are read and displayed in the current value list.The above display shows that one page of parameters has been successfully read, and the green tick on the far left indicates that a parameter has been read.

- 、One-click read all parameters

Click the buttonto read the parameters in all parameter groups at one time, and update all parameters to display in the current value list.

As shown in the figure above, the dialog box displays the total number of parameters to be read and the number of completed reading. Due to the large number of parameters, the entire reading and updating process takes a long time.

- 、Write a parameter

- For example: change the parameter to 9 (Modbus communication setting), click the drop-down box to select 9, press the Enter key on the

- keypad, or click the other blanks in the table to confirm the writing.

The following shows that the parameter writing is successful:

- 、Write Current Page Parameters

Click the button to enter the operation interface for writing the parameters of the current parameter group. For example ，the dialog box prompts whether all parameters need to be written. Click Yes (Y) to start writing. When the write operation is completed, you can use the leftmost prompt to determine whether the write is successful.

Note: Reserved parameters are automatically skipped and will not be written.

5）、One-click write all parameters

Click the button，this operation will write all the parameter settings of the current parameter groups into the AC Drive. Since there are many parameters to be written, the whole writing operation process takes a long time.

Tip: When the writing operation of all parameters is completed, you can check whether the writing of all parameters is successful by checking the log. Some parameters do not support communication writing.

6）、Save Parameters

Click the button，Keep the current value on the interface in the opened parameter configuration table. After closing the software, when the software is opened next time, the last saved parameter can be displayed in the current value example.

7）、Export Parameters

Click the button，this function saves all parameter settings in the current interface in the form of an Excel configuration table. As shown in the figure below, the parameters will be kept in a file with a suffix of .xls.

8）、Import parameters

Click the button，this function is used to load the saved configuration table of different current values or the parameter configuration table of different series of AC Drives into the software; as shown in the figure below, you can choose to load the configuration table of SD600 series, so as to conduct communication access to the SD600 series AC Drive.

Note: Make sure the form is closed before importing the form, otherwise an error will be reported.

4. Real-time Monitoring

- 、Monitoring options

Click the icon on the software interface，enter the real-time monitoring interface as shown below:

Click to select a monitoring point，select the data items to be monitored, and use the following figure to increase or decrease the data to be monitored.

- 、Software Communication Start and Stop Control

When the AC Drive is set to communication mode for running operation (F00.01=4), various control operations can be selected from the communication control drop-down options in the interface, such as start-stop, jog and other operations; for example, after selecting forward running , the ac drive starts to run forward, and at the same time, in the monitoring parameter column, the selected monitoring parameters will also start to update in real time .

- 、Communication Parameter Setting

When some parameters are set to be given by communication mode, they can be set and given in the parameter setting box on the right side of the figure above, for example, when F01.00 = 9 (A frequency command is given by communication mode). Input 45.00 in the "set frequency" box, click set, then the set frequency of the ac drive is changed to 45.00Hz.

5. Fault Analyze

- 、Read Fault

When the drive has a fault, you can click the "Read Fault" button to get the current fault information. The following figure shows when an external fault occurs:

Through the display content, you can find out the cause of the failure and the way of troubleshooting. When troubleshooting is done by clicking "Fault reset" button to clear the current fault.

- 、Fault Reset

When a fault occurs, the fault can be reset through the "fault reset" button in the interface, so that the fault reset can be achieved without operating the keypad.

6.View logs

By clicking the button, you can view the current communication data interaction status information.

Logs can be cleared and saved.

7.Exit the system

When you no longer want to use the virtual display oscilloscope, you can exit the system through the close button or button in the upper right corner.